## Sheet1
ELECTRICAL Frequently Asked Questions & their answers
Sr. No. | Questions | Answers
A | Distribution Boards
1 | What is DB stands for ? | Distribution Board
2 | What are Various type of Db available? | 1)SPN DB
2) TPN DB
3)Per Phase Isolation (PPI) DB
4) Vertical TPN (VTPN)
5)Flexi/Row DB
6) 7 Segment DB
7) Phase Selector DB
3 | What is mounting height of DB? | The DB shall not be more than 1.8m from floor level.
4 | Details of SPN DB | Single Phase & Neutral Distribution Board • Available in 4,6,8,12,16 & 18way • Suitable for flush & surface mounting • IP30 for single door & IP43/54 for double door • IK 8 for concealed DB & IK 9 for Mivan DB • With provision for DP MCB/Isolator/RCCB/RCBO as incomer & SP MCB as outgoings • For Residential ,school & hospital application- In order to provide protection against electric shock due to leakage current for human being, 30mA RCCB/RCBO-Incomer of DB • For all other Building , 100mA RCCB/RCBO-Incomer of DB
5 | Details of TPN DB | Three Phase & Neutral Distribution Board • Available in 4,6,8,12 & 16 way • Suitable for flush & surface mounting • IP30 for single door & IP43/54 for double door • With provision for FP MCB/Isolator/RCCB/RCBO as incomer & SP MCB as outgoings
6 | Details of PPI DB | Three Phase & Neutral (TPN)Distribution Board with Per Phase Isolation • Available in Horizontal PPI 4,6,8,12 & 16ways and Tier PPI 6,8,10,12 & 16ways • Suitable for flush & surface mounting • IP43/54 for double door • With provision for FP MCB/Isolator/RCCB/RCBO as incomer, DP RCCB/RCBO as Sub incomer & SP MCB as outgoings
7 | Flexi/Row DB | Flexi/Row Flexibility to mount incoming & outgoing as per requirement • Available in 2,3 rows in 14 modules per row & 4 rows in 14/16 modules per row • Suitable for flush & surface mounting • IP30 for single door & IP43/54 for double door • With provision to mount modular devices as per requirement
8 | Vertical TPN (VTPN) | Vertical Busbar for Three Phase & neutral supply distribution • Available in 4,6,8,12 & 16 ways • Suitable for flush & surface mounting • IP30 for single door & IP43/54 for double door • With provision FP MCB/isolator/RCCB/RCBO as incomer & SP/TP MCB as outgoing
B | Meter Room
1 | What are various type of meters in residential building? | Single phase meter, Three phase meter & Three phase CT meter
2 | Space required for single phase meter- | 300mm (H) x 300mm (W)
3 | Space required for Three phase meter- | 600mm (H) x 450mm (W)
4 | Space required for Phase CT meter- | 1200mm (H) x 450mm (W)
5 | Height of energy meter display- | Between 750mm & 1800mm.
C | Conduit/cable tray
1 | What are the various type of conduits & where they are used? | 1)PVC conduit
2)MS
3)GI
2 | What are various standard size available in Conduits? | Dia 20mm , 25mm, 32mm, 40mm, 50mm
3 | What are the type of cable tray? | 1) Perforated cable tray
2) Ladder cable tray
3) Solid Cable tray
Load calculation
| Determination of load of residential/Commercial/Industrial premises | Residential- 75 W/sq.mt.
Commercial with central air-conditioning - 200 W/sq.mt.
All other commercial establishments - 150 W/ sq.mt.