## Sheet1
HVAC Frequently Asked Questions & their answers (HVAC)
Sr. No. | Questions | Answers
1 | What is the HVAC stands for ? | H - Heating, V - Ventilation, AC - Air Conditioning
2 | What are the systems available for Air Conditioning ? | 1) DX Split System - Normally used for residential apartments and small shops / Offices,
2) DX Package Units - Used in Big offices / Shops
3) DX VRF / VRV System - Used in Big apartments / Shops / Offices / Commercial spaces / Resorts
4) Chiller Systems (Air Cooled / Water Cooled) - Used in the commercial spaces / Office buildings / Hotel Buildings / Resorts.
3 | How to calculate AC TR based on the thumb rule ? | 1) For residential apartments - 160 to 180 Sqft per TR
2) For Shops - 150 Sqft per TR
1) For Anchor Shops - 130 to 150 Sqft per TR
1) For Office area - 130 to 150 Sqft per TR
1) For Multi Purpose hall & Restaurants - 110 to 130 Sqft per TR
4 | What are the parameter to be considered for Cooling Load (if not provided by client) ? | 1) Clear Glass U Value - 0.6 BTU/ ft2-hr-°F
2) Clear Glass shading coefficient - 0.4
3) Glazed Glass U Value - 0.36 BTU/ ft2-hr-°F
4) Glazed Glass shading coefficient - 0.24
5) External wall U Value - 0.36 BTU/ ft2-hr-°F
6) Partition wall U Value - 0.39 BTU/ ft2-hr-°F
6) Insulated Roof U Value - 0.15 BTU/ ft2-hr-°F
7) Uninsulated floor U Value - 0.31 BTU/ ft2-hr-°F
5 | What is the ventilation rates to be considered in cooling load? | Ventilation rates to be referred from table no 6.2.2.1 chapter ASHRAE 62.1.
6 | What is the maximum Pipe length to be considered while planning the DX IDU & ODU? | For normal DX 10meter max and for inverter type DX it is 30meter.
7 | What is the minimum distance to be kept between top of Hiwall unit and Slab Bottom? | Minimimim 150 mm gap required between slab/false ciling bottom and unit top (in special condition it can be 100mm).
8 | What is the maximum length of DX AC drain pipe to be considered? And what is the slop to be maintain | Maximum 3 meter length to be considered not more than that. 1:150 or 200 slop to be maintain in AC drain.
9 | What is the maximum throw range of Hiwall unit? | Maximum throw range of hiwall unit is 12 feet (3.6 meter) (2.0 TR Hiwall unit throw range is 5 meter)
10 | What is the Sleeve dia to be provided for refrgerent pipes routed through beam | if single circuite is running through beam then minimimum 100 mm dia sleeve required and if 2 circuits are running through beam then minimimum 150mm dia sleeve required
11 | Where to provide main supply for DX AC? | MCB to be provided at ODU and 16 Amps socket to be provided at IDU.
12 | What is the DX Unit Sizes (IDU and ODU)? | Check Standard units sizes layout saved in the folder
13 | What is the VRV Unit Sizes (IDU and ODU)? | Check Standard units sizes layout saved in the folder
14 | What Is the minimum space required behinde the DX ODU | Standered 300 mm gap required behinde the ODU from wall (minimum 250mm)
15 | What is the over all space required for DX ODU | Check the snip as follows
16 | What is the over all space required for VRF ODU