## PHE FAQ's
PHE Frequently Asked Questions
Sr. No. | Questions | Answers
1 | What is PHE Stands for ? | Public Health Engineering
2 | What is Fixture Unit (FU) ? | FU is measurement unit in Plumbing application which indicates the hydraulic load imposed by that respective fixture on the plumbing installation based on discharging rate, frequency of use and time of operation. It is not a flow rate unit but a design factor. It differs for water supply & drainage applications. Refer Table 2 & Table 18 from NBC Volume-II, Part 9, Plumbing application.
3 | How to calculate water demand ? | Refer section 4.1 & Table 1 from NBC Volume-II, Part 9, Plumbing application.
4 | What is Gravity & Hydropneumatic method of Water supply in the tower ? | Gravity system - It is widely used & most cost effective method of Water supply in the modern world in which First Municipal water is collected in the Underground tank. After which with the help of Pumping system water is transferred to Overhead tank usually planned on Terrace Top. From OH Tank the water is transferred to Toilet/Kitchen fixtures through Gravity. Hydropneumatic System - In this system, Water is directly transferred to Toilet/Kitchen Fixtures from UG tank with the help of Hydro-pneumatic pump set.
5 | How to calculate water supply pipe size ? | There are two methods of Water supply Pipe size calculation : 1. Volumetric Flow Rate Q (m3/s) = Area of Pipe (m2) x Velocity of water (m/s) 2. Hazen Williams Formula :
6 | How to calculate drainage pipe size ? | For Drainage Pipe size calculation use Manning Equation :
7 | What is Air vent (Air Release valve) & its funtion ? | ARV is used in the Plumbing intallation to release the trapped air in the system. It should be installed in the top of the Riser/Downtake & in the Ringmain.
8 | How to select Vent stack size ? | In no case the vent stack should be below Dia 75mm. For High rise Tower Refer Table 17 from NBC Volume-II, Part 9, Plumbing application.
9 | How to select Overflow pipe dia ? | Overflow pipe should be always one size higher than the Inlet pipe. If not possible provide 2# of same size overflow pipe.
10 | What is the difference between Pressure Reducing valve & Pressure Relief valve ? | Pressure Reducing Valve : It is the devise used to Reducing the water pressure from upstream to downstream. Pressure Relief Valve : It is the devise used to release the excessive pressure formed in the Pump outlet side to ensure the safety of installation & personnel.
11 | What to ensure while planning the Typical Toilet water supply & drainage pipe route ? | For Water Supply : 1. Route should be minimum with less bends & fittings. 2. Flush Valve or Flush tank (Confirmation from client/Engineer) 3. Geyser type (Instant or storage), capacity (3/15/25 Liter) & location (Above False ceiling - with trap door/On wall mounting/In shaft mounting) 4. Isolation valve should be accesible from Window itself. 5. Pipe to be run above false ceiling or concealed in the wall. 6. Type of construction - Brick or RCC Mivan (Accordingly Groove planning to be done as per Standards) 7. Hot water connection should always on left side. For Drainage : 1. Minimum clear 150mm Ledge wall to be provided for Flush tank or If soil pipe is away from the wall adjacent to wall. 2. If WC is mountd on the Shaft wall then outlet should be taken directly outside or else drop in the ledge wall to be considered. 3. Minimum 100 mm Ledge wall to be proposed. 4. Minimum bend to be provided (Specially in the Soil pipe). 5. Underslung / Sunken to be confirmed beforehand. 6. Minimum 250mm Sunken to be proposed in Single Toilet. 150mm for Kitchen/Utility/Balcony area. 7. Proposed Strip sunk in the Kitchen instead of pocket sunk unless client is adamant. 8. Double Y Fitting to be avoided 9. Only Multi Floor Trap (50mm water seal) to be proposed. 10. Waste outlet sleeve in sunken should be kept as per trap location (BOS at 75mm from sunk bottom if near or 25mm if far) 11. Soil sleeve in sunken should be kept at 25mm from sunk bottom.
12 | What are the most important things while considering / finalising the Hydropneumatic Pumps ? | 1. Hydropneumatic Pump set should be factory fitted and should be of Skid mounted. 2. Positive suction is must. 3. MOC : Body CI/CS, Impeller - SS/Bronze, Shaft - SS 3. Fixed Speed system to be used only for Smaller flow rate (Like Bungalow, low cost rehab tower etc. 4. For Medium scale project Single VFD to be proposed with Cascade operation. 5. For High end project Each Pump with Independent VFD to be proposed. 6. Pressure Vessel design & size should be as per pump vendor.
13 | Why we have to provide Vent connection to First & Last Inspection chamber ? | To ensure that Foul smell do not enter/get trapped in the system. It should have a clear passage to get released in the atmosphere.
14 | How to select Inspection chamber size ? | Starting Chamber : 900 x 450mm - Till 0.9m depth 900 x 600mm - From 0.9m to 1.2m depth Circular 900mm dia - From 1.2m to 1.8m depth Circular 1200mm dia - From 1.8m to 2.4m depth Circular 1500mm dia - From 2.4m to 4.5m depth Circular 1500mm dia - From 4.5m and above